Specific Fire Protection Requirements Affecting each occupancy class, per NFPA 101 (2006 ed)

| Ch | Type of Occupancy | Fire Alarm System | Radio Call Box | Sprinkler System |
| --- | --- | --- | --- | --- |
| 11 | All High Rise Buildings | Voice-Evac | Required | Spkl & Standpipe |
| 12 | New Assembly | Required if >300 persons. Voice Evac Required | Reqd > 300 persons | Reqd >100 persons |
| 13 | Existing Assembly | Required if >300 persons. Voice Evac Required | Reqd > 300 persons | Reqd >100 persons |
| 14 | New Educational | Req'd if >1,000sq' or > 1 classroom or < 30' from another building | Required | Partial coverage required below level of exit discharge |
| 15 | Existing Educational | Req'd if >1,000sq' or > 1 classroom or < 30' from another building | Required | Partial coverage required if students present below level of exit discharge |
| 16 | New Day Care | Req'd if > 1 room | Required | Required if unprotected openings |
| 17 | Existing Day Care | Req'd if > 1 room | Req'd if >100 clients | Required if unprotected openings |
| 18 | New Health Care | Required | Required | Required |
| 19 | Existing Health Care | Required | Required | Required |
| 20 | New Ambulatory Health Care | Required | Required | Required |
| 21 | Existing Ambulatory Health | Required | Required | Required |
| 22 | New Detention & Correctional | Required | See 101:22.3.4.3.2 | See NFPA 101:22.3.5 |
| 23 | Existing Detention & Correctional | See 101: 23.3.4 | See 101:23.3.4 | See NFPA 101:23.3.5 |
| 24 | 1&2 Family Dwellings | AC/DC Smoke / Co Alarms | Not Required | Not Required |
| 26 | Lodging or Rooming Houses* | Required | Not Required | Required |
| * Except for existing S/D system, if 1 pull station / floor |  |  | Not Required | Not Required |
| 28 | New Hotels & Dorms | Required | Req'd in high rises | Required |
| 29 | Existing Hotels & Dorms | Required | Req'd in high rises | Req'd in high rises |
| 30 | New Apartment Buildings | >3 stories or > 11 apts*. | Required | Required* |
| *Required unless each apt has an outside door and 1 hour fire separation between apartments |  |  |  |  |
| 31 | Existing Apt Buildings | >3 stories or > 11apts* | Required | Not Required |
| *Required unless each apt has an outside door and 1 hour fire separation between apartments |  |  |  |  |
| 32 | New Res. Board & Care | Required | Required | Required |
| 33 | Existing Res. Board Care | Required* | Required** | Not Required |
| * Except for interconnected smoke detector system featuring at least one pull station per floor |  |  | **Continuosly attended location with telephone may be permitted by the Fire Marshal. |  |
| 36 | New Mercantile | >30,000 square feet | >30,000 square feet | >12,000 sq' or >2 stories |
| 37 | Existing Mercantile | >30,000 square feet | >30,000 square feet | >15,000 sq' /story or 30K |
| 38 | New Business | >2 stories or >50 people above the level of exit discharge or > 300 people total | Not Required | Only portable fire extinguishers are required |
| 39 | Existing Business | >2 stories or > 100 people above the level of exit discharge or > 300 people total | Not Required | Only portable fire extinguishers are required |
| 40 | Industrial Occupancies | >25 people above the level of exit discharge or >100 people total | Not Required | Not Required |
| 41 | Storage Occupancies | Required for ordinary or high hazard Required if > 100,000 square feet Not Required if sprinkler installed | Not Required | Not Required |